## Slide 1
EEE 414
Electrical Services Design
A Project on Electrical Design on Seven-Storeyed Building
Project By
1706040- Habibullah Khan
1706041- Deb. Indronil Sajib
1706042- Md Monirul Islam
1706044- Shuvro chowdhury
1706051- Sariha Noor azad
1706055- Adib Md Ridwan

## Slide 2
Floor Plan – Ground Floor

## Slide 3
Floor Plan – 1st & 2nd Floor

## Slide 4
Floor Plan –third and above Floor

## Slide 5
Floor Plan –third and above Floor

## Slide 6: Ground Floor (Substation)
Sample Calculation for Light Bulbs and Fans
Lights:
  Illuminance ,E = 150 lux
  Area , A = (6.6 * 16.01) sq-ft = 105.666 sq-ft = 105.666/10.76 m2 = 9.82 m2
  Lumen of the light bulbs (10 Watt LED bulb), F = 1250 lm
  Light loss factor* Utilization factor = LLF * UF = 0.75
  Number of lights per illuminare, n=1
  Number of light bulbs required = N
  So, E = => N = = = 1.5712 ≈ 2

## Slide 7: Ground Floor (Garage)
Sample Calculation for Light Bulbs and Fans
Lights:
  Illuminance ,E = 100 lux
  Area , A = (17.01 * 35.1+ 22.8*17.01) sq-ft = 984.528 sq-ft = 983.528/10.76 m2 = 91.5m2
  Lumen of the light bulbs (10 Watt LED bulb), F = 1250 lm
  Light loss factor* Utilization factor = LLF * UF = 0.75
  Number of lights per illuminare, n=1
  Number of light bulbs required = N
  So, E = => N = = = 9.76 ≈ 10

## Slide 8: First Floor (Garage)
Sample Calculation for Light Bulbs and Fans
Lights:
  Illuminance ,E = 100 lux
  Area , A = (43.8 * 34.6) sq-ft = 1515.48 sq-ft = 1515.48/10.76 m2 = 140.84 m2
  Lumen of the light bulbs (10 Watt LED bulb), F = 1250 lm
  Light loss factor* Utilization factor = LLF * UF = 0.75
  Number of lights per illuminare, n=1
  Number of light bulbs required = N
  So, E = => N = = = 15.02 ≈ 16

## Slide 9: 3rd floor (Guestroom)
Sample Calculation for Light Bulbs and Fans
Calculation of light bulbs and fans:
Lights:
  Illuminance of Drawing room , E = 200 lux
  Area , A = (12.005 * 11.5) sq-ft = 138.0575 sq-ft = 138.0575/10.76 m2 = 12.83 m2
  Lumen of the light bulbs (10 Watt LED bulb), F = 1250 lm
  Light loss factor* Utilization factor = LLF * UF = 0.75
  Number of lights per illuminare, n=1
  Number of light bulbs required = N
  So, E = => N = = = 2.737 ≈ 3
Fans:
  Number of fans = =1.380575

## Slide 10: 3rd floor (bedroom)
Sample Calculation for Light Bulbs and Fans
Calculation of light bulbs and fans:
Lights:
  Illuminance of Drawing room , E = 200 lux
  Area , A = (11.5 * 12.6) sq-ft = 144.9 sq-ft = 144.9/10.76 m2 = 13.47 m2
  Lumen of the light bulbs (10 Watt LED bulb), F = 1250 lm
  Light loss factor* Utilization factor = LLF * UF = 0.75
  Number of lights per illuminare, n=1
  Number of light bulbs required = N
  So, E = => N = = = 2.87 ≈ 3
Fans:
Number of fans = =1.449

## Slide 11
Electrical Appliances and Fixture / Fittings Schedule

## Slide 12
Fitting and Fixtures Layout – Ground Floor

## Slide 13
Fitting and Fixtures Layout – first and second Floor

## Slide 14
Fitting and Fixtures Layout – Typical Floor

## Slide 15
Conduit Schedule
Label | Wire size | Wire current rating | Conduit radius
C1 | 2*1.5 rm BYM | 5A | ¾”
C2 | 4*1.5 rm BYM | 5A | ¾”
C3 | 6*1.5 rm BYM | 5A | ¾”
C4 | 8*1.5 rm BYM | 5A | 1”
C5 | 10*1.5 rm BYM | 5A | 1”
C6 | 12*1.5 rm BYM | 5A | 1.25”
C7 | 14*1.5 rm BYM | 5A | 1.25”
C8 | 2*2.5 rm BYM + 2.5 rm BYA ECC | 10A | ¾”
C9 | 2*4 rm BYM + 4 rm BYA ECC | 15A | ¾”
C10 | 4*2.5 rm BYM + 2*2.5 rm BYA ECC | 10A | 1”
C11 | 6*2.5 rm BYM + 3*2.5 rm BYA ECC | 10A | 1.25”
C12 | 2*1.5 rm BYM + 1.5 rm BYA ECC | 5A | ¾”
C13 | 4*1.5 rm BYM + 2*1.5 rm BYA ECC | 5A | ¾”
C14 | 6*1.5 rm BYM + 3*1.5 rm BYA ECC | 5A | 1”
C12,9 | 2*16 rm BYM + 16 rm BYA ECC+ 2*4 rm BYM + 4 rm BYA ECC | 5A, 15A | 1.25”
C9,9 | 4*4 rm BYM + 2*4 rm BYA ECC | 30A | 6/4”
Legends for conduit:

## Slide 16
Conduit Layout – Ground Floor

## Slide 17
Conduit Layout – first and second Floor

## Slide 18
Conduit Layout – third and above Floor

## Slide 19
Conduit of TV, Telephone and Data Network

## Slide 20
Calculation For Lightning Protection System
Building Length – 48’-8” Building width -35’-4”
Air conductor calculation: One conductor at each of the 4 corners.
    Maximum distance between 2 air conductor is 25’.
    So, along width we need 2 air conductors at the middle.
    And along length 2 air conductor is needed.
    The perimeter of the building is 2*(48.6+35.3)=167.8 feet
    So down conductor required is 167.8/100=2
    So, Down conductor required is 2
    For safety purpose we have taken 3 down conductor.

## Slide 21
Lightning Protection System

## Slide 22: Current Calculation
LED bulb:
  Power rating of each LED bulb is 10W. Current flow through light bulb, I= = 0.048A
LED tube light:
  Power rating of each LED tubelight is 20W (130 lm per watt, so 1250 lm is almost 10W). Current flow through tube light, I= = 0.096A
Exhaust fan (EF):
  Power rating of each Exhaust fan is 20W (5W-35W). Current flow through EF, I= = 0.12A
2 pin 5A socket at switchboard level (SS) :
  This is for charging a mobile (2-5W)) or laptop(20-50W) or desktop computer (200W). So, maximum current flow through SS, I= = 1.16 A
Power Sockets:
  P: These are redundant power sockets for living rooms for washing machine, iron or other high power accessories , let standard SP MCB rating = 15A, so 2X4 rm BYM + 4 rm BYA ECC wire is needed.
  Q: These are redundant power sockets for living rooms for washing machine, iron or other high power accessories , let standard SP MCB rating = 15A, so 2X4 rm BYM + 4 rm BYA ECC wire is needed.

## Slide 23: Current Calculation
Ceiling Fan:
  Power rating of each a 56 inch wing ceiling fan is 80 W. Current flow through ceiling fan, I= = 0.386 A
  Power rating of each a 36 inch wing ceiling fan is 75 W. Current flow through ceiling fan, I= = 0.362 A

## Slide 24
Switch Board Connection Diagram – Ground Floor

## Slide 25
Circuit Current calculation– Ground Floor
CKT1:
Component connecting to SB1 are LC1,LC2,TB1,TB2 and SS1.
Total current for circuit1=2*0.048+2*0.096+1.16=1.448A < 5A
So 2x1.5 rm BYM +1.5 rm BYA ECC cable are required.
CKT2:
Component connecting to SB2 are LC4,LC5 and SS2.
Total current for circuit2=0.048+0.048+1.16=1.256A < 5A
So 2x1.5 rm BYM +1.5 rm BYA ECC cable are required.
CKT3:
Component connecting to SB3 are LC12,LC13,LC14,LC15,LC16,LC17.
Total current for circuit3=6*0.048=0.288A < 5A
So 2x1.5 rm BYM +1.5 rm BYA ECC cable are required.
CKT4:
Component connecting to SB4 are L1,F1, SS3.
Total current for circuit4=0.048+0.362+1.16=1.57A < 5A
So 2x1.5 rm BYM +1.5 rm BYA ECC cable are required.

## Slide 26
Emergency Switch Board Connection Diagram – Ground Floor

## Slide 27
Emergency Circuit Current calculation– Ground Floor
ECKT1:
Component connecting to ESB1 are LC3,TB3,TB4 and ESS1.
Total current for circuit1=0.048+2*0.096+1.16=1.4A < 5A
So 2x1.5 rm BYM +1.5 rm BYA ECC cable are required.
ECKT2:
Component connecting to ESB2 are LC6,LC7,LC8,LC9,LC10,LC11.
Total current for circuit2=6*0.048=0.288A < 5A
So 2x1.5 rm BYM +1.5 rm BYA ECC cable are required.
ECKT3:
Component connecting to ESB3 are LC19,LC20,ESS2
Total current for circuit3=2*0.048+1.16=1.256A < 5A
So 2x1.5 rm BYM +1.5 rm BYA ECC cable are required.

## Slide 28
Sub Distribution Board(SDB) Diagram – Ground Floor

## Slide 29
SDB Circuit Current calculation– Ground Floor
CKT1 =1.448A
CKT2 =1.256A
CKT3 =0.288A
CKT4 =1.57A
Total Current = 4.562A < 5A
So 2x1.5 rm BYM +1.5 rm BYA ECC cable are required

## Slide 30
Emergency Sub Distribution Board(ESDB) Diagram – Ground Floor

## Slide 31
ESDB Circuit Current calculation– Ground Floor
ECKT1 =1.44A
ECKT2 =0.288A
ECKT3 =1.256A
Total Current = 2.984A < 5A
So 2x1.5 rm BYM +1.5 rm BYA ECC cable are required

## Slide 32
Switch Board Connection Diagram – 1st and 2nd Floor

## Slide 33
Emergency Switch Board Connection Diagram – 1st and 2nd Floor

## Slide 34
Sub Distribution Board(SDB) Diagram – 1st and 2nd Floor

## Slide 35
Emergency Sub Distribution Board(ESDB) Diagram – 1st and 2nd Floor

## Slide 36
Switch Board Connection Diagram – Third Floor SDB1

## Slide 37
Switch Board Connection Diagram – Third Floor ESDB1

## Slide 38
Sub Distribution Board(SDB) Diagram – third Floor

## Slide 39
SDB Current Calculation– Third Floor SDB1
CKT1 =2.656A
CKT2 =1.663A
CKT3 =1.57A
CKT4 =1.352A
CKT5 =1.352A
CKT6 =0.096A
P = 15A * 3
Total Current = 8.689 + P x0.5 = 31.189A
So 2x16 rm BYM +16 rm BYA ECC cable are required

## Slide 40
Emergency Sub Distribution Board(ESDB) Diagram – third Floor

## Slide 41
ESDB Current Calculation– Third Floor ESDB1
ECKT1 =1.6904A
ECKT2 =1.6183A
ECKT3 =1.328A
ECKT4 =1.6904A
ECKT5 =1.6904A
ECKT6 =0.096A
Q = 15A * 3
Total Current = 8.096 + Q x0.5 = 30.596A
So 2x16 rm BYM +16 rm BYA ECC cable are required

## Slide 42
Main Distribution Board diagram

## Slide 43
POWER Calculation for MDB
Floor0:
P=VI*PF=230*4.56*0.9=943.94 Watt
Floor1:
P=VI*PF=230*3.136*0.9=649.152Watt
Floor2:
P=VI*PF=230*3.136*0.9=649.152Watt
Floor3:
P=VI*PF=230*31.189*0.9=6.5KWatt
Floor4:
P=VI*PF=230*31.189*0.9=6.5KWatt
Floor5:
P=VI*PF=230*31.189*0.9=6.5KWatt
Floor6:
P=VI*PF=230*31.189*0.9=6.5KWatt
Floor7:
P=VI*PF=230*31.189*0.9=6.5KWatt
PUMP:
p = 5kw
Total power=39.7KW

## Slide 44
Emergency Main Distribution Board diagram

## Slide 45
POWER Calculation for EMDB
Floor0:
P=VI*PF=230*3.024*0.9=625 Watt
Floor1:
P=VI*PF=230*4.104*0.9=849.5Watt
Floor2:
P=VI*PF=230*4.104*0.9=849.5Watt
Floor3:
P=VI*PF=230*30.596*0.9=6. 3KWatt
Floor4:
P=VI*PF=230*30.596*0.9=6. 3KWatt
Floor5:
P=VI*PF=230*30.596*0.9=6. 3KWatt
Floor6:
P=VI*PF=230*30.596*0.9=6. 3KWatt
Floor7:
P=VI*PF=230*30.596*0.9=6. 3KWatt
Lift:
P = 8Kw
Total power=41.8KW

## Slide 46
Reference

## Slide 47: Thank You